## Slide 1: Control Accessories

## Slide 2: Control Accessory- G-Way
Remote control (ON/OFF) of FCU via BMS.
Unit error indication via BMS and wired control panel .
Unit operation status monitoring via BMS.
Maximum point to point communication bus up to 1000m.
DIP switch setting for control or monitoring function.
User retains the ability to control the other settings.
(MODE, FAN SPEED, AIR SWING, TIMER, SET TEMPERATURE etc).
Specification

## Slide 3: Control Accessory- G-Way
The G-way system consists of :
  Main Board controller (U1.4 / W1V3 / L208A / U1SB125)
  Display control panel (wired / wireless controller)
  G-way controller
Specification

## Slide 4: Control Accessory- G-Way
To Main Board
Dip Switch
Dry Contact Output 1
RELAY1
RELAY2
Dry Contact
Input
Dry Contact Output 2
To Wired Control Panel
Terminal Blocks
G-way Controller
Unit On/Off Indicator
Dry Contact Switch
Unit Error Indicator
BMS
Relay rating:
30VDC, 3A
250VAC, 2A
COM
NO
NC
COM
NO
NC
960m
CN2
CN1
Specification
  Connection diagram
Notes: Where is the 12V comes from? (to energize the Relay)

## Slide 5: Control Accessory- G-Way
Types of Operation | DSW2 Setting
Control & Monitor (Ext. Switch Closed = ON A/C) | 0000
Control & Monitor (Ext. Switch Open = ON A/C) | 0010
Monitoring only | 0001
DSW2
Specification
  Hardware configuration

## Slide 6: Control Accessory- G-Way
When DSW2 is set to 0000 or 0010, FCU can only be ON/OFF via BMS. No display control panel/handset will be able to ON/OFF the FCU. However when FCU is ON, FCU parameters are set-able using display control panel/handset.
When DSW2 is set to 0001, FCU can be ON/OFF using display control panel/handset and BMS cannot ON/OFF the unit. However all three settings allow for monitoring of the alarm or operation status of the FCU (ON/OFF)
Specification
  Hardware configuration

## Slide 7: Thank you